# Guide for Hazardous Areas

Hazardous areas according to ATEX and IECEx Zones

Hazardous areas according to North American classes and divisions

Zones - define the type of explosive atmosphere as well as the likelihood of an explosive atmosphere being present

0 - Explosive gas atmosphere present continuously or for long periods

1 - Explosive gas atmosphere likely to occur in normal operation

2 - Explosive gas atmosphere not likely to occur in normal operation but may be present for short periods

20 - Explosive dust atmosphere present continuously or for long periods

21 - Explosive dust atmosphere likely to occur in normal operation

22 - Explosive dust atmosphere not likely to occur in normal operation but may be present for short periods

Classes - define the type of explosive atmosphere

I - A location made hazardous by the presence of flammable gas or vapour that may be present in the air in quantities sufficient to produce an explosive or ignitable mixture

II - A location made hazardous by the presence of combustible or electrically conductive dust

III - A location made hazardous by the presence of easily ignitable fibers or flyings in the air, but not likely to be in suspension in quantities sufficient to produce ignitable mixtures

Divisions - define the likelihood of an explosive atmosphere being present

1 - A location where a classified hazard exists or is likely to exist under normal conditions

2 - A location where a classified hazard does not normally but is possible to appear under abnormal conditions

In Canada new installation must now use the Class / Zone system of Zones instead of Divisions. Existing installations may use either system.

In the USA, all installations can use either the Class / Division or the Class / Zone system.

| ATEX equipment group | ATEX equipment category and environment type | Zone classification ATEX / IECEx | Required equipment protection level (EPL) | Class / Zone classification US / Canada | Class / Division classification US / Canada |
| --- | --- | --- | --- | --- | --- |
| I | M1 | N/A | Ma | N/A | Mining |
|  | M2 |  | Mb |  |  |
| II | 1G | Zone 0 | Ga | Class 1, Zone 0 | Class I, Division 1 |
|  | 2G | Zone 1 | Gb | Class 1, Zone 1 |  |
|  | 3G | Zone 2 | Gc | Class 1, Zone 2 | Class I, Division 2 |
|  | 1D | Zone 20 | Da | Class 1, Zone 20 | Class II, Division 1 |
|  | 2D | Zone 21 | Db | Class 11, Zone 21 |  |
|  | 3D | Zone 22 | Dc | Class 11, Zone 22 | Class II, Division 2, Class III |